The emission standards of pollutants for semiconductor industry

(Second draft version for comment)

Abstract:

- This is the first amendment of The emission standards of pollutants for semiconductor industry (DB31/374-2006). The main revises include: (1) adjust the standard classes for wastewater effluent standards; (2) adjust the control methods for air emission standards; (3) add new pollutant control items; (4) tight up the standard limits for some pollutant items; (5) add concentration limits at reference point for air pollutants at enterprise boundary; (6) update analytical methods for some pollutant items.

- This standard stipulate the monitoring and supervision of water discharge and air emission for semiconductor industry, which include discrete device and IC manufacturing, packaging & testing facilities.

- For new semiconductor facilities, they must implement the standard when it comes into effect. For existing semiconductor facilities, they must begin to implement the standard, one or two years after.

- The wastewater effluent limits are:

| No. | Item | Efflunet limit for direct effluent(mg/L) | Efflunet limit for indirect effluent(mg/L) | Sampling point |
| --- | --- | --- | --- | --- |
| 1 | pH | 6-9 | 6-9 | The final discharge point |
| 2 | SS | 50 | 400 |  |
| 3 | Oil | 3 | 15 |  |
| 4 | CODCr | 60 | 500 |  |
| 5 | BOD5 | 20 | 300 |  |
| 6 | TOC | 20 | 150 |  |
| 7 | NH3-N | 5 | 45 |  |
| 8 | TN | 15 | 70 |  |
| 9 | TP | 0.5 | 8 |  |
| 10 | LAS | 3 | 20 |  |
| 11 | Cyanide | 0.2 | 0.5 |  |
| 12 | Sulfide | 1 | 1 |  |
| 13 | Fluoride | 8 | 20 |  |
| 14 | Cu | 0.5 | 1 |  |
| 15 | Zn | 1.5 | 1.5 |  |
| 16 | Boron | 2.0 | 3.0 |  |
| 17 | Pb | 0.1 |  | The treatment equipment discharge point |
| 18 | Cd | 0.05 |  |  |
| 19 | Cr | 0.5 |  |  |
| 20 | Cr6+ | 0.1 |  |  |
| 21 | As | 0.2 |  |  |
| 22 | Ni | 0.1 |  |  |
| 23 | Ag | 0.1 |  |  |
| 24 | Co | 1.0 |  |  |
| 25 | Sn | 2.0 |  |  |
| 26 | Tl | 0.005 |  |  |

- From Jan. 1st 2024, the semiconductor concentrated wastewater treatment facilities must meet the standard limit for toxicity as follows:

| No. | Item | Reference limits | Sampling point |
| --- | --- | --- | --- |
| 1 | Acute toxicity of zebra fish eggs | ≤6 | The final discharge point |

- The air pollutants emission standards are:

| No. | Item | Emission limits（mg/m3） | Emission rate（kg/h）(1) | Sampling point |
| --- | --- | --- | --- | --- |
| 1 | H2SO4 | 5 | 2.6 | Vent stacks of waste gas treatment facilities |
| 2 | HCl | 10 | 1.4 |  |
| 3 | HF | 1.5 | 0.59 |  |
| 4 | Cl2 | 3 | 1.5 |  |
| 5 | HCN | 0.5 | 0.05 |  |
| 6 | Tin and its compounds | 1 | 0.1 |  |
| 7 | Ammonia | 15 | 4.9 |  |
| 8 | Benzene | 1 | 0.1 |  |
| 9 | Benzene homologues | 8 | 0.8 |  |
| 10 | VOCs(2) | 40 | 4 |  |
| 11 | NMHC | 40 | 4 |  |
| 12 | PM | 10 | 2.4 |  |
| 13 | NOx | 50 | 4 |  |
|  |  | 150 | - | Vent stacks of waste gas thermal oxidation treatment unit |
| Note： (1) No apply to IC manufacturing facilities manufacturing of 12-inch wafers on 40nm and less process. (Comply with the approved EIA reports) (2) Apply to IC manufacturing facilities only. |  |  |  |  |

- The concentration limits at reference point for air pollutants at enterprise boundary are:

| No. | Item | Emission limits（mg/m3） |
| --- | --- | --- |
| 1 | HCN | 0.024 |
| 2 | Cl2 | 0.1 |
| 3 | HCl | 0.15 |
| 4 | NMHC | 4.0 |